## Retentive Force
Facility Name |  | Rampart General Hospital |  |  |  |  | Tester Name |  | James Smith
Address |  | 127 Main Street |  |  |  |  | Tester Company |  | Generic Testing Inc.
City, Province |  | Mayberry, ON
[7 empty] | Meter Manufacturer |  | Chatillon
[7 empty] | Meter Model Number |  | DFX2-010-NIST
[7 empty] | Meter Serial Number |  | 16788240011324
|  |  | Pin Retention (N) |  |  |  | Meter Calibration Date |  | 2015-12-09
|  |  | 5% | 5% | 5% | 5%
|  | Receptacle Identification | 1.1 | 2.2 | 2.2 | 13 | Retention | Physical
Date | Circuit | Room/Location | G | N | L | LN | Result | Condition | Recommendation
2016-03-16 | 2B-32-A | 204B West wall by door | 4.8 | 7.1 | 7.7 | 14.8 | 1 | 1 | None
2016-03-16 | 2B-32-A | 204B Left nightstand | 3.5 | 4.4 | 3.4 | 7.8 | 0 | 1 | Replace
2016-03-16 | 2B-32-B | 204B East wall by cabinet | 5.2 | 6.11 | 6.5 | 13.7 | 1 | 1 | None
2016-03-16 | 2B-32-B | 204B Right of bed | 1.15 | 3.7 | 4.1 | 13.2 | 2 | 1 | Replace
2016-03-16 | 2B-32-C | 204B Beside cabinet | 1.7 | 2.8 | 10.3 | 13.67 | 1 | 0 | Replace
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
?
Note:
Usage:
Disclaimer:
Receptacle retentive force: the ground pin retentive force shall be not less than 1.1 N (4.0 ounce-force). The retentive force of each plug blade shall be not less than 2.2 N (8.0 ounce-force). The combined retentive force of each plug’s blades shall be not less than 13 N (47.0 ounce-force). See Clause 5.6.6.2 of CSA Z32.
Compliance with these requirements shall be verified using a receptacle retention tester designed for the purpose
  a) on completion of new construction, major renovations, or receptacle replacement;
  b) in basic care areas at least every two years after initial verification; and
  b) in intermediate and critical care areas at least every year after initial verification.
See Clause 5.6.6.1 of CSA Z32.
Although Optum Engineering makes every reasonable effort to ensure their accuracy at the time of this publication, information and formulae described herein are subject to error or omission and to change without notice.
Optum Engineering provides the information, specifications, and formulae herein on an "AS IS" basis, with no representations or warranties, whether express, statutory or implied. In no event will Optum Engineering be liable for any damages (including consequential, indirect, incidental, special, punitive, or exemplary damages) whatsoever, even if Optum Engineering has been advised of the possibility of such damages, whether in an action under contract, negligence or any other theory, arising out of or in connection with the use, or inability to use, the information, specifications, or formulae described herein.
Optum Engineering believes this template to be in compliance with CSA Z32. Regulatory information is for guidance purposes only. Product users are responsible for determining the applicability of legislation and regulations based on their individual usage of this template.
Percentages listed below "Pin Retention (N)" indicate the amount required to exceed the minimums specified in the CSA Z32 standard. For example, 5% for a 1.1 N (minimum specification) ground pin means that measurements between the required minimum of 1.1 N and 1.1+5% N (or 1.155 N) are considered "Marginal" and replacement is recommended. Measurements below the CSA Z32 minimums signify a failure and replacement is recommended.
Under column headings G (ground), N (neutral), L (line), and LN (line and neutral), enter the measured force without units (numeric values only). For example, if the ground pin retention measures 3.6 N, enter 3.6.
The state of receptacles may also be used to trigger a recommended replacement. Under the column “Physical Condition”, enter either a 0 or 1. A 0 entry indicates a bad receptacle (cracked, or chipped for example), and a 1 indicates a good receptacle. The “Recommendation” column will display either “None” or “Replace” based on results entered.
For more information, visit: www.allerasystems.com
Marginal plugs (based on above listed percentages) are highlighted.
Failed plugs (not meeting minimum requirements) are highlighted and triggered for replacement.
Generated recommendation based on retention results and physical condition.
Results determined automatically based on minimum requirements and tolerance.